## Slide 1: TA Station Power
Team Meeting, 11/10/2015

## Slide 2
Autonomous Power System – In the field
Why Lithium?
-Significant weight and volume savings (41.9Wh/lb vs 21.25Wh/lb)
-Improved cold weather and self discharge performance
-Improved lifespan
-Increased cost and complexity

## Slide 3
LiFePO4
LiFePO4
LiFePO4
LiFePO4
LiFePO4
LiFePO4
Battery 1
AGM (Lead acid)
AGM (Lead acid)
AGM (Lead acid)
AGM (Lead acid)
Battery 2
Solar Panel
Solar Panel
Solar Panel
MCU
Charge controller
Load2
Autonomous Power System Block Diagram
Energy Input
MCU
Load1

## Slide 4
Voltage
Temperature
Balance control
Cell 1
Voltage
Temperature
Balance control
Cell 2
Voltage
Temperature
Balance control
Cell 3
Voltage
Temperature
Balance control
Cell 4
Battery Management System
LiFePO4 Battery
Battery Terminals
Lithium Battery Block Diagram
Four 3.4V, 180Ah cells in each battery
Voltage and temperature sensing on each cell
Active cell balancing to prevent capacity mismatch
Sub millisecond control of output terminals
  Short circuit, under/over voltage, under/over temperature protections
Issues:
CC MCUs susceptible to damage during programming
Switch that controls battery output has failed in many batteries deployed in the field